## Tabelle1
Application scenarios	MODE	COMMAND		PV	Grid	Battery
		EMSPowerMode	EMSPowerSet	Power priority (Green is the control object)
System shutdown	Stopped	0x00FF	NA
	Note :Stop working and switch to wait mode

Self-use	Auto	0x0001	NA
	Note: PBattery =PInv - Pmeter – Ppv (Discharge/Charge)
	The battery power is controlled by the meter power when the meter communication is normal.

Control the battery to / keep charging	Charge-PV	0x0002	Xmax [2]	High	Low [1]	Energy In
	Note :PBattery =Xmax + PV (Charge)
	Xmax is to allow the power to be taken from the grid, and PV power is preferred. When set to 0, only PV power is used.

Control the battery to / keep discharging	Dischg+PV	0x0003	Xmax	High	Energy Out	Low
	Note : PBattery = Xmax (Discharge)
	Xmax is the allowable discharge power of the battery. When the power fed into the grid is limited, PV power will be used.

The inverter is used as / a unit for power grid / energy scheduling	Import-AC	0x0004	Xset [3]	Low	High	Energy In
	Note :PBattery = Xset + PV (Charge)
	Xset refers to the power purchased from the power grid. The power purchased from the grid is preferred. If the PV power …
	Export-AC	0x0005	Xset	High	Energy Out	Low
	Note : PBattery = Xset (Discharge)
	Xset is to sell power to the grid. PV power is preferred. When PV energy is insufficient, the battery will discharge. PV …

Off-grid reservation / mode	Conserve	0x0006	NA
	Note : PBattery = PV (Charge)
	In on-grid mode, the battery is continuously charged, and only PV power (AC Couple model takes 10% of the rated power …

Off-Grid Mode	Off-Grid	0x0007	NA
	Note : PBattery =Pbackup – Ppv (Charge/Discharge)
	Forced off-grid operation (Disconnect from grid)

No battery mode for / hybrid inverter	Battery standby	0x0008	NA
	Note : PBattery =0 (Standby)
	The battery does not charge and discharge

Regional energy / management	Buy Power	0x0009	Xset	Low	High	Energy In / Out
	Note :PBattery = PInv – (Pmeter + Xset)– Ppv (Charge/Discharge)
	When the meter communication is normal, the power purchased from the power grid is controlled as Xset. When the PV …
	Sell Power	0x000A	Xset	High	Energy Out	Low
	Note : PBattery = PInv – (Pmeter – Xset) – Ppv (Charge/Discharge)
	When the communication of electricity meter is normal, the power sold from the power grid is controlled as Xset, PV …

Force the battery to / work at set power value	Charge-BAT	0x000B	Xset	High	Low	Energy In
	Note : PBattery = Xset (Charge)
	Xset is the charging power of the battery. PV power is preferred. When PV power is insufficient, it will buy power from the …
	Discharge-BAT	0x000C	Xset	Low	Energy In	High
	Note : PBattery = Xset (Discharge)
	Xset is the discharge power of the battery, and the battery discharge has priority. If the PV power is too large, MPPT will …

Note: / [1] for low-priority energy sources, when the battery charging power is limited or the rated output power of the inverter is limited, the load shall be ... / [2] Xmax represents the upper limit of the power control value, and the actual power will be adjusted according to the working condition. / [3] Xset represents the target value of power control, and the actual power must reach the set value.